## Sheet1
CT Green Bank RFP for YCI Fuel Cell Installation
Question and Answers
Questions are due on 6/20 by 5pm
Question | Date Submitted | Response
Please provide details on 22.8 kV utility switchgear. This should include bus current rating, size of all breakers (including trip settings), etc. | 2022-06-20
Please provide details on Generator 4160V generator switchgear. This should include bus rating current, size of all breakers (including trip settings), etc. | 2022-06-20
Can we utilize 52-G3 to connect new fuel cell to the facility's electrical system? | 2022-06-20
What is the size and technical specification of the 4160V to 22.8 kV transformer that connects Generator switchgear to Main utility switchgear? | 2022-06-22
Can we get a copy of drawing E6.2? | 2022-06-23
Would it be possible to get an extension on the RFP due date? Even with an expedited turn-around of the questions being submitted, there would only be a little over a week of time to put together a complete proposal. Please consider extending the due date at least another week. | 2022-06-20
Where is the incoming network MPOE? is Cellular/4G/5G allowed on site for remote system monitoring? | 2022-06-20
Is 30-minute generator testing done weekly and also monthly, island mode only during monthly testing (weekly generator testing is connected to grid only, no island mode | 2022-06-20
Where is the nearest city water connection? what is the water pressue is psi? | 2022-06-20
Who is the financier of this project? What is the role of the Green Bank? | 2022-06-20 | Applicants are expected to incorporate financing, in the form of a third-party owned structure, into their bid. The CT Green Bank's has 3 primary roles (1) administer the RFP (2) act as the initial counter-party to the Department of Correction for the PPA or selected financing structure. The PPA (or other contract) will then be assigned to the winner of the RFP (3) provide debt to the system owner at the terms described in the RFP. It is not required that bidders make use of CT Green Bank debt
The delivery term start day is mentioned as April 1, 2022. Has this been extended? | 2022-06-20 | The delivery term start date (DTSD) has not been extended and is not eligible for an extension. A LREC contract is valid for one year from the DTSD, when the Automatic Termination Date is reached. It is CGB and DOC's intent to extend that Automatic Termination Date in advance of the 3/30/23 termination date.
Do we have a copy of Attachment 1, Contract Provisions, per 2.8.3 (p.28) of the RFP? | 2022-06-20
Can excess power produced by the Fuel Cells be exported to the Grid? | 2022-06-20
Will the preferred bidder be able to reassign the PPA to a separate entity? | 2022-06-20
Please confirm the following preferred order of operations when generator testing is performed to minimize Demand Charges as discussed at the walk through: 1. Generators come one line, while grid connected. 2. Fuel Cells Trip to Idle (no export Power) 3. Grid Tie Breaker Open, Generator Island Testing performed 4. Grid Tie Breaker Closed 5. Fuel Cells come to full load while generators are still operating 6. Generators go offline | 2022-06-20
Will the site generators be sufficient to supply all power required during electrical tie-in Shut Down? | 2022-06-20
Can fuel cells be located in field beyond buried water tanks, approximately 80' from building? | 2022-06-20
Where can domestic water be sourced from? | 2022-06-20
Can you please provide recent utility bills? For electricity please provide both the Distribution (Eversource) and any third party supplier if applicable. This will give us insight into current energy costs | 2022-06-20
A 1400 kW system is a good fit for facility heat offset and also demand charge offset, however it exceeds recent kWh facility use over a yearly period. Has anything been set regarding the price of power that is exported to the utility? | 2022-06-20
Please provide Electric Utility meter number | 2022-06-20
Please provide 480v one lines for Building 10 | 2022-06-21